Ultrasonic sensor Ultrasonic sensor                                         UM300-18GM-E5-V1

| Technical data |  |
| --- | --- |
| General Specifications |  |
| Sensing distance 30…300mm |  |
| Adjustment range 30…300mm |  |
| Unusable area 0…30mm |  |
| Standard target plate 100mm×100mm |  |
| Transducer frequency About 300 kHz |  |
| Response delay About 65ms |  |
| Indicators/Operating means |  |
| LED Blue solid: object in evaluation range flashing: program function object detected |  |
| LED Red flashing: fault or program function no object detected |  |
| Electrical specifications |  |
| Operating voltage UB 10…30VDC,ripple10%ss |  |
| No-load supply current ≤15mA |  |
| Output |  |
| Output type 1 switch output PNP NO/NC,programmable |  |
| Resolution 0.11mm at max.sensing range |  |
| Deviation of the characteristic curve ±1% of full-scale value |  |
| Repeat accuracy ±0.1% of full-scale value |  |
| Load impedance >1k Ohm Maximum switching current 200 mA (reverse polarity protection) |  |
| Temperature influence ±1.5% of full-scale value |  |
| Ambient conditions |  |
| Ambient temperature -25…70℃ |  |
| Storage temperature -40…85℃ |  |
| Mechanical specifications |  |
| Protection grade IP67 |  |
| Connection Connector M12x1,4-PIN | 1 BN=BROWN 2 WH=WHITE 3 BU=BLUE 4 BK=BLACK V1 Connector |
| Material Housing brass,nickel-plated |  |
| Transducer epoxy resin/hollow glass sphere mixture; Polyurethane foam |  |
| Weight 50g Compliance with standards and directives |  |
| Standard conformity EN 60947-5-2:2020 |  |

Adjusting the switching points

The ultrasonic sensor features a switch output with two teachable switching points. These are set by applying the supply voltage - UB or + UB to the TEACH-IN input. The supply voltage must be applied to the TEACH-IN input for at least 1 s.LEDs indicate whether the sensor has recognised the target during the TEACH-IN procedure. Switching point A1 is taught with - UB,A2 with +UB.  Five different output functions can be set.

- Window mode, normally-open function.

- Window mode, normally-closed function.

- One switching point,normally-open function

- One switching point,normally-closed function.

- Detection of objet presence.

Switching point, Setting distance only after power on. The internal clock can assure can't be changed after 5 mins when power

on. If want to change the switching point, the user can only setting the request distance after power restart.

| TEACH-IN window mode,normally-open function -Set target to near switching point -TEACH-IN switching point A1 with - UB -Set target to far switching point -TEACH-IN switching point A2 with + UB |  |  |  |
| --- | --- | --- | --- |
| TEACH-IN window mode,normally-closed function -Set target to near switching point -TEACH-IN switching point A2 with + UB -Set target to far switching point -TEACH-IN switching point A1 with - UB |  |  |  |
| TEACH-IN switching point, normally-open function -Set target to near switching point -TEACH-IN switching point A2 with + UB -Cover sensor with hand or remove all objects from sensing range -TEACH-IN switching point A1 with - UB |  |  |  |
|  |  |  | Curve1:flat surface 100mm×100mm Curve2:round bar,Φ25mm |
| TEACH-IN switching point, normally-closed function -Set target to near switching point -TEACH-IN switching point A1 with - UB -Cover sensor with hand or remove all objects from sensing range -TEACH-IN switching point A2 with + UB |  |  |  |
| TEACH-IN detection of objects presence -Cover sensor with hand or remove all objects from sensing range -TEACH-IN switching point A1 with - UB -TEACH-IN switching point A2 with + UB |  |  |  |
| Default setting of switching point A1=blind range,A2=nominal distance |  |  |  |
| LED displays |  |  |  |
| Displays in dependence on operating mode | Red LED | Blue LED |  |
| TEACH-IN switching point Object detected No object detected Object uncertain(TEACH-IN invalid) | Off flashes off | flashes off off |  |
| Normal operation | off | Switching state |  |
| Fault | on | Previous state |  |

Installation conditions

If the sensor is installed at the environment temperature fall below 0℃,It should do well on the protective measures. In case of direct mounting of the sensor in a through hole using the steel nuts, it has to be fixed at the middle of the housing thread.