Manual for High Temperature Pressure Transmitter

I.Product Overview

High temperature pressure transmitters use high-precision and high-sensitivity pressure sensitive components. Through a stable, reliable, and anti-interference amplification circuit, the pressure signal of the measured medium is converted into standard analog or digital signals. With exquisite packaging technology and perfect detection processes, the product ensures excellent performance and is widely used in industrial automation fields such as petroleum, chemical, metallurgical, environmental protection, measurement, automation control engineering, and production process detection.

II. Technical parameters

Test medium: liquid or gas compatible with the material

Range:- Any interval within 0.1~250MPa

Accuracy level: 0.1% FS 0.25% FS 0.5%FS

Stability: ± 0.25% FS/year ± 0.5% FS/year

Output signal: 4~20mA 0~10V, RS485 communication

Working voltage: 12~36V DC (calibration: 24V ± 5%, ripple<1%)

Power supply impact: less than 0.01%/V of the output range

Working temperature:- 20~80℃

Compensation temperature:- 20~80℃

Temperature impact: ± 1.55% FS/year ± 3.0% FS/year

Overload capacity: 300%

Threaded interface: M20 * 1.5, G1/2, 1/2NPT, etc

R=U−140.02−RDLoad resistance: 4-20mA

(Among them: U is the power supply voltage, RD is the internal resistance of the cable)

Warning: It is strictly prohibited to disassemble the transmitter without authorization!

It is strictly prohibited to press the measuring element membrane with fingers!

It is strictly prohibited to insert any sharp objects into the pressure hole!

| 4-20mA（2 wires） | Hirschmann pin ① 24V+ | Hirschmann pin ② | Hirschmann pin ③ | Hirschman pin G |
| --- | --- | --- | --- | --- |
| 4-20mA（2 wires） | Red 24V+ | Black output | \ | \ |
| 0-10V（3 wires） | Hirschmann pin ①24V+ | Hirschmann pin ② 24V- | Hirschmann pin ③ | Hirschman pin G |
| 0-10V（3 wires） | Brown 24V+ | Black 24V- | Blue output | \ |
| RS485 | Hirschmann pin ①24V+ | Hirschmann pin ② 24V- | Hirschmann pin ③ A | Hirschman pin GB |
| RS485 | Red 24V+ | Black 24V- | Yellow A | Green B |

Wire Definition

Wire installation

Unscrew the screw and remove the Husman connector

Use a Phillips screwdriver to pry out the junction box from the disassembly slot

Insert the cable from the outlet and connect it according to the terminal

definition corresponding to the output signal

Assemble and restore the Husman connector, and tighten the wire cap

matters needing attention

It is prohibited to measure media that are incompatible with the material

of the transmitter;

Ensure that the power supply voltage meets the product requirements

and wire according to the instructions;

The installation of the transmitter should be in a ventilated and dry place,

avoiding direct exposure to strong light and rain;

Pay attention to using snake skin pipes or iron pipes to protect the outgoing cables,

or raising the cable rack;

It is recommended to power on for at least 10 minutes to achieve optimal product performance;

Ensure that the pressure source is turned off when disassembling the transmitter to prevent the medium from spraying out;

This product is not explosion-proof and may cause major accidents when used in explosion-proof areas;

Troubleshooting

| Fault phenomenon | reason | resolution |
| --- | --- | --- |
| Zero point output exceeded accuracy error range | ·Membrane damaged ·The back pressure pipe of the gauge type product is not connected to the atmosphere | ·Need to return to the factory for maintenance ·Small pressure products should use gas cables and the gas ducts should be connected to the atmosphere |
| The collection device has no display or displayed value Inconsistent with actual pressure | ·Wiring error ·The transmitter has no signal output ·Error in calibration of output signal and pressure range | ·Check the wiring according to the wiring method corresponding to the output signal of the transmitter ·Measure the output signal of the transmitter ·Recalibrate the acquisition equipment according to the range and output of the transmitter label |
| Output signal and actual pressure mismatch | ·The medium or ambient temperature exceeds the specified range ·Power supply voltage exceeds the limit ·Excessive external load | ·Install a cooling device at the pressure inlet or move the transmitter to a low-temperature environment for retesting ·Adjusting the power supply voltage ·Adjusting external loads |
| When the pressure is constant output irregular jump | ·The transmitter is not grounded ·Strong on-site radio frequency interference ·Unused shielded cable | ·Use shielded cables and ground the shielding layer ·Reliable connection between transmitter and ground |

After-sale service

Customers who order our products can enjoy a one-year warranty period;

If the product malfunctions during the warranty period and our company detects it as a quality issue, we will bear all the repair costs;

Damage to components or pressure diaphragms caused by failure to follow the instructions in this manual or unauthorized disassembly of the product is not covered by the product warranty.

After the product malfunctions, please contact our company and confirm the repair. Please attach the following information:

Product malfunction phenomenon;

Description of the on-site environment for product use;

Delivery address and contact information;